## Slide 1: Chapter 2 Transformers
Edit by Chi-Shan Yu

## Slide 2: Chapter 2 Transformers
Types and construction of transformers
The ideal transformer
Theory of operation of real single-phase transformers
Equivalent circuit of a transformer
Transformer voltage regulation and efficiency
Transformer taps and voltage regulation
The autotransformer
Three-phase transformer
Three-phase transformers using two transformers
Instrument transformers

## Slide 3: Transformers
The transformer winding connected to the power source is called the primary winding or input winding
The winding connected to the loads is called the secondary winding or output winding
….tertiary winding

## Slide 4: Why transformers are important to modern life
The transformer ideally changes one ac voltage level to another voltage level without affecting the actual power supplied.
The transformer can be used in distribution system for efficiency issues.
  The step-up transformer decreases the line current and decreases the power loss on power line.
  The transmission/distribution system with transformer can keep high efficiency

## Slide 5: Voltage levels used in Taipower system
Low voltage : 110V, 220V, 380V
High voltage (HV): 11.4kV, 22.8kV (distribution system)
Extra high voltage (EHV): 69kV, 161kV (transmission system)
Ultra high voltage (UHV): 345kV (transmission system)

## Slide 6: Types and construction of transformers
Core-form: consists a simple rectangular laminated piece of steel with the transformer winding wrapped around two sides of the rectangle
Shell-form: consists three legs laminated core with winding wrapped around the center leg

## Slide 7: Core material and eddy current
The core is constructed of thin laminations electrically isolated from each other in order to minimize the eddy currents.
Eddy current:

## Slide 8: Special purpose transformers
Unit transformer: used for voltage up from generator to transmission system.
Substation transformer: used for voltage down from transmission to distribution
Distribution transformer: used for voltage down from distribution to actual used levels
Potential transformer (PT): 110V at secondary side
Current transformer (CT): 5A at secondary side

## Slide 9: The ideal transformer characteristics

## Slide 10: The ideal transformer characteristics
Where a=Np/Ns is the turns ratio
Energy balance relation
Phasor relation
The turns ratio a only effects the magnitude not the angle

## Slide 11: Dot convention in ideal transformer

## Slide 12: Power in an ideal transformer

## Slide 13: Power in an ideal transformer

## Slide 14: Impedance transformation through a transformer

## Slide 15: Analysis of circuits containing ideal transformers
All the current and voltage are all referred to one side (primary side)
Note the dot convention for current direction
Impedance transformation

## Slide 16: Example 2-1

## Slide 17: Example 2-1

## Slide 23: Induced voltage and flux linkage l
The induced voltage
The flux linkage
Simplified by average flux
The final induced voltage

## Slide 24: Voltage relation between primary and secondary derived from Faraday’s law

## Slide 25: Voltage relation
Induced voltage on each side
Primary side flux
Secondary side flux

## Slide 26: Voltage relation
Induced voltage on primary side
Induced voltage on secondary side

## Slide 27: Induced voltage relation - Induced by mutual flux

## Slide 28: Terminal voltage relation - Neglecting the leakage flux

## Slide 29: Modeling the leakage flux by leakage inductance

## Slide 30: Modeling the leakage flux by leakage inductance

## Slide 31: Theory of operation of real single-phase transformers – secondary side open
Secondary side is open circuit
Input voltage and current to measure hysteresis curve
Flux is proportional to vp and magnetomotive force is proportional to ip
ip(t) = 0 for ideal transformer

## Slide 32: Magnetization current in real transformer
The magnetization current iM is used to generate mutual flux fM
While secondary side is opened, the current measured at primary side contains two parts and is called the excitation current iex
  Magnetization current iM: to generate mutual flux
  Core loss current ih+e : hysteresis and eddy currents

## Slide 33: Magnetization curve

## Slide 34: Magnetization current

## Slide 35: Magnetization current

## Slide 36: Core loss current

## Slide 37: Excitation current iex

## Slide 38: Current ratio on a transformer

## Slide 39: Polarity of the magnetomotive force
Current flows into “Dot” will produce a positive magnetomotive force
Current flows out “Dot” will produce a negative magnetomotive force

## Slide 40: The net magnetomotive force and magnetic circuit

## Slide 41: Ideal transformer

## Slide 42: The assumptions from real to ideal transformer

## Slide 43: The equivalent circuit of a transformer – to model the non-ideal characteristics

## Slide 44: Modeling excitation current and copper loss
The hysteresis and eddy currents is in-phase with input voltage (modeled as a shunt resistor Rc)
The magnetization current is lagging input voltage by 90 degrees (modeled as a shunt inductor Xm)
The copper loss can be modeled as the series resistors Rp and Rs

## Slide 45: The resulting equivalent circuit

## Slide 46: Impedance transform to primary or secondary side

## Slide 47: Approximate equivalent circuit

## Slide 48: Neglecting excitation current

## Slide 49: Measure the equivalent circuit parameters
There are two types of measurements used for determination the equivalent circuit parameters
Open circuit test – used to measure excitation branch
Short circuit test – used to measure series branch

## Slide 50: Open circuit test

## Slide 51: Open circuit test
Under the open circuit condition, all the input current flows through the excitation branch (Since the current is small, the test usually performs at high voltage side)

## Slide 52: Short circuit test

## Slide 53: Short circuit test
At secondary side short circuit condition, the input voltage must be a very low value to prevent input large short circuit current (usually performs at low voltage side)

## Slide 54: Example 2-2

## Slide 58: Transformer voltage regulation and efficiency

## Slide 59: How to calculate the voltage regulation – transformer phasor diagram
Use the phasor relation to obtain the voltage regulation

## Slide 60: Phasor diagram - lagging

## Slide 61: Phasor diagram - unit

## Slide 62: Phasor diagram - leading

## Slide 63: Approximation

## Slide 64: Transformer efficiency

## Slide 65: Transformer efficiency

## Slide 66: Example 2-5

## Slide 74: Transformer taps and voltage regulation
The taps of transformer is used to change the effective turns ratio of transformer

## Slide 75: TCUL and voltage regulator
The tape changing under load (TCUL) is a transformer with the ability to change taps while power is connected to it
The voltage regulator is the TCUL with voltage sensing circuitry that automatically change taps to maintain the output voltage level

## Slide 76: The autotransformer
Continuously tune the output voltage magnitude
The size of auto transformer is smaller than the size of conventional transformer
Output terminal is not electrical isolation

## Slide 77: The step-up connection of autotransformer from conventional transformer

## Slide 78: The step-down connection of autotransformer

## Slide 79: Voltage and current in both coils
Coil voltage and current in Nc and Nse still follow the voltage and current relation
The autotransformer terminal voltage and current

## Slide 80: Terminal voltage and current relation of autotransformer

## Slide 81: Terminal voltage and current relation of autotransformer

## Slide 82: Apparatus power rating advantage in autotransformer
There are two types of rating
  Power rating on terminals Sio
  Power rating on windings Sw
Terminals power rating Sio
Winding power rating Sw

## Slide 83: Apparatus power rating advantage in autotransformer
Relation

## Slide 84: Example 2-7

## Slide 87: Autotransformer summarize
When two voltages are fairly close to each other
The power advantage is very large
There is a direct physical connection between primary and secondary sides.
The autotransformer is a convenient and inexpensive way to tie nearly equal two voltages together
The electrical isolation of two sides is lost

## Slide 88: Example 2-8

## Slide 90: Three-phase transformer – three single-phase transformer banks

## Slide 91: Three-phase transformer – one three-lags transformer banks

## Slide 92: Three types of terminal connection

## Slide 93: Wye-wye connection

## Slide 94: Wye-wye connection

## Slide 95: Wye-wye connection

## Slide 96: Wye-wye connection

## Slide 97: Solving the unbalance and 3rd harmonic problems in wye-wye connection
Solid ground the neutral of transformers: solve the unbalance problem and support a return path to the 3rd harmonic component.
Add a D-connected third winding: Since 3rd harmonic components are in-phase in each branch of D-connection, 3rd harmonic components will be limited in D-connection as the circulating current.

## Slide 98: Wye-delta connection

## Slide 99: Wye-delta connection

## Slide 100: Wye-delta connection summarize
No 3rd harmonic component problem:
There are phase difference between each sides
In United state, the secondary voltage will lag the primary voltage 30 degrees

## Slide 101: Phase analysis

## Slide 102: Delta-wye connection

## Slide 103: Delta-wye connection

## Slide 104: Phase analysis

## Slide 105: Delta-wye connection
Common connection:
  Used on three-wire (delta) to four wire (wye)
  Used to isolate ground on wye side from source ground on delta side

## Slide 106: Delta-wye or wye-delta
Common for wye-delta step-up transformer banks in generating plants
Common for delta-wye step-down banks in substation

## Slide 107: Delta-delta connection

## Slide 108: Delta-delta connection

## Slide 109: Three-phase transformation using two transformers

## Slide 110: V-V connection

## Slide 111: Power rating of D-D connection

## Slide 112: Power rating of V-V connection

## Slide 113: Comparison of power rating
The power rating comparison
Where is the power rating ?
  The existing reactive power will consume the power rating

## Slide 114: Open Y-open D connection

## Slide 115: Scott-T connection – railroad applications
While in railroad applications, there always need two-phase power system for supporting northbound and southbound rails respectively.

## Slide 117: T-T three phase connection

## Slide 118: T-T three phase connection

## Slide 119: Transformer rating and relative problems
Voltage rating
  Prevent the over-voltage insulation problem
  Prevent the saturation of magnetization curve

## Slide 121: Frequency limitation
If a 60Hz transformer operates on 50Hz, its applied voltage must be reduced by one-sixth
If a 50Hz transformer operates on 60Hz, its applied voltage may rise 20 percents.

## Slide 122: Inrush current problem

## Slide 123: Instrument transformer
Potential transformer (PT)
Current transformer (CT)

## Slide 124: Recap
You must know the magnetization current, core loss current and excitation current
You must know the equivalent circuit of real transformer
Voltage regulation and efficiency of transformer
The differences between four types connection of three-phase transformer
V-V connection, Scott T connection